## Blast Chiller
Description | Quarterly | Annually | Requirement | Comments
Leak check entire system |  | X
Compressors
Vibration | X | X | Visually check refrigeration compressors and compressor rack for visible siqns of vibration
Oil Residue | X | X | Visually check refrigeration compressors, refrigeration compressor rack, and condensinq units for visible siqns of oil residue
Excessive Heat |  | X
Oil Level | X | X | Look at each sight glass and verify that oil level is between 1/3 and 1/2 of glass
Foam in Oil | X | X | Look at each sight glass for foam.
Looseor missing Covers | X | X | Look at all cover, cover plates, etc.
Noise Level | X | X
Valve Caps | X | X | Look at each valve and ensure that all valves have valve cap in place
Test refrigeration system for non-condensibles |  | X
Execute oil acid test |  | X
High/Low Pressure Switches | X | X | Verify settings and operation of switch
Oil Failure Switch | X | X | Verify settings and operation of switch
Check oil pressure |  | X | Confirm within manufacturer's recommendations
Air Cooled Condenser
Fan motor | X | X | Look at condenser fan to verify that it is rotating
Fan guards | X | X | Inspect for broken, missing, or loose fan guards
Loose panels/components | X | X | Inspect all panels and covers
Valve caps | X | X | Inspect all valves to ensure that valve caps are in place
Clean or dirty? | X |  | Inspect inlet side of condenser for dirt, cotton, or other debris that will impact air flow
Fin condition | X |  | Inspect condenser coil surface for damaged or loose fins
Air flow? | X | X | Verify that air can flow/ is flowing through condenser
Clean Condensers |  | X | Contractor to pressure wash condenser
Pressure switches | X | X
Fan Cycling/ condenser split | X | X | If system is so equipped, verify operation and settings
Sensors/Transducers intact |  | X | If system is so equipped, verify that temperature sensors are attached to piping
Oil Reservoir/ Oil Separator
Inspect oil reservoir/oil separator | X | X | Inspect vessle for oil residue
Verify oil level | X | X | Look at sight glass and verify oil level
Filter Driers
Change Driers |  | X
Suction Filters
Change Filters |  | X
Oil Filters
Change Oil Filters |  | X
Cooler/Freezer Boxes
Condensation issues | X | X | Inspect interior, and exterior of box for condensation issues or ice build up
Ice build up an floor | X | X | Inspect freezer floor along walls, and across doorways for ice build up
Door gaskets | X | X | Inspect door gasket for signs of damage, tears, or flattening
Door sweeps | X | X | Verify that door sweeps on cooler or freezer doors drag on the floor
Door closure mechanism | X | X | Verify operation of door closure mechanism
Latch and strike (inside and outside) | X | X | Inspect door latch and strike to ensure operation and that when closed, door is held tiaht to door fram
Strip Curtains
Inspect for Damage | X | X | Inspect door curtains for signs of damage
Evaporators
Inspect of ice buildup | X | X | Inspect each evaporator for signs of ice build up
Fans spinning | X | X | Inspect each evaporator fan to ensure operation
Fan guards | X | X | Inspect for broken, damaged, or loose fan guards
Vibration | X | X | Inspect fan motor and fan assembly for vibration
Fan bearing noise | X | X | Listen to each fan motor for bearing noise
Fan rotation direction | X | X | Verify fan rotation
Coil damage/ fin condition | X | X | Inspect each coil sheet for damage
Is the evaporator dirty |  | X | Check to see if evaporator coil is dirty
Cleaning of evaporators |  | X
Evaporator Drain Lines
Drains clean |  | X
Heat tape operation | X | X | Verify operation of heat tape
Piping System
Vibration |  | X | Visually inspect refrigeration piping system and look specificall for vibration, shakinq, movement, torn insulation
Torn insulation |  | X | Visually inspect piping system for signs of torn insulation
Condensation/Ice build up |  | X | Inspect piping system for signs of moisture, ice build up
Hangers- verify pipe is touching hangers, insulation is not crushed, etc |  | X | Inspect piping system to ensure that hangers are not damaged and are supporting pipe

## Low Temp Rack
Zero Zone System - Low Temp Rack B Model OPS-SO714M2-91-404A PM Maintenance of System and all Affilitated Equipment
|  | Quarterly | Annually | Requirement | Comments
Leak check entire system |  |  | X
Compressors
| Vibration | X | X | Visually check refrigeration compressors and compressor rack for visible siqns of vibration
| Oil Residue | X | X | Visually check refrigeration compressors, refrigeration compressor rack, and condensinq units for visible siqns of oil residue
| Excessive Heat |  | X
| Oil Level | X | X | Look at each sight glass and verify that oil level is between 1/3 and 1/2 of glass
| Foam in Oil | X | X | Look at each sight glass for foam.
| Looseor missing Covers | X | X | Look at all cover, cover plates, etc.
| Noise Level | X | X
| Valve Caps | X | X | Look at each valve and ensure that all valves have valve cap in place
| Test refrigeration system for non-condensibles |  | X
| Execute oil acid test |  | X
| High/Low Pressure Switches | X | X | Verify settings and operation of switch
| Oil Failure Switch | X | X | Verify settings and operation of switch
| Check oil pressure |  | X | Confirm within manufacturer's recommendations
Air Cooled Condenser
| Fan motor | X | X | Look at condenser fan to verify that it is rotating
| Fan guards | X | X | Inspect for broken, missing, or loose fan guards
| Loose panels/components | X | X | Inspect all panels and covers
| Valve caps | X | X | Inspect all valves to ensure that valve caps are in place
| Clean or dirty? | X |  | Inspect inlet side of condenser for dirt, cotton, or other debris that will impact air flow
| Fin condition | X |  | Inspect condenser coil surface for damaged or loose fins
| Air flow? | X | X | Verify that air can flow/ is flowing through condenser
| Clean Condensers |  | X | Contractor to pressure wash condenser
| Pressure switches | X | X
| Fan Cycling/ condenser split | X | X | If system is so equipped, verify operation and settings
| Sensors/Transducers intact |  | X | If system is so equipped, verify that temperature sensors are attached to piping
Oil Reservoir/ Oil Separator
| Inspect oil reservoir/oil separator | X | X | Inspect vessle for oil residue
| Verify oil level | X | X | Look at sight glass and verify oil level
Filter Driers
| Change Driers |  | X
Suction Filters
| Change Filters |  | X
Oil Filters
| Change Oil Filters |  | X
Cooler/Freezer Boxes
| Condensation issues | X | X | Inspect interior, and exterior of box for condensation issues or ice build UD
| Ice build up an floor | X | X | Inspect freezer floor along walls, and across doorways for ice build up
| Door gaskets | X | X | Inspect door gasket for signs of damage, tears, or flattening
| Door sweeps | X | X | Verify that door sweeps on cooler or freezer doors drag on the floor
| Door closure mechanism | X | X | Verify operation of door closure mechanism
| Latch and strike (inside and outside) | X | X | Inspect door latch and strike to ensure operation and that when closed, door is held tiaht to door fram
Strip Curtains
| Inspect for Damage | X | X | Inspect door curtains for signs of damage
Evaporators
| Inspect of ice buildup | X | X | Inspect each evaporator for signs of ice build up
| Fans spinning | X | X | Inspect each evaporator fan to ensure operation
| Fan guards | X | X | Inspect for broken, damaged, or loose fan guards
| Vibration | X | X | Inspect fan motor and fan assembly for vibration
| Fan bearing noise | X | X | Listen to each fan motor for bearing noise
| Fan rotation direction | X | X | Verify fan rotation
| Coil damage/ fin condition | X | X | Inspect each coil sheet for damage
| Is the evaporator dirty |  | X | Check to see if evaporator coil is dirty
| Cleaning of evaporators |  | X
Evaporator Drain Lines
| Drains clean |  | X
| Heat tape operation | X | X | Verify operation of heat tape
Piping System
| Vibration |  | X | Visually inspect refrigeration piping system and look specificall for vibration, shakinq, movement, torn insulation
| Torn insulation |  | X | Visually inspect piping system for signs of torn insulation
| Condensation/Ice build up |  | X | Inspect piping system for signs of moisture, ice build up
| Hangers- verify pipe is touching hangers, insulation is not crushed, hangers have |  | X | Inspect piping system to ensure that hangers are not damaged and are supporting pipe

## Medium Temp Rac
Zero Zone System -Medium Temp Rack A Model OPS-SO714M2-91-404A PM Maintenance of System and all Affilitated Equipment
|  | Quarterly | Annually | Requirement | Comments
Leak check entire system |  |  | X
Compressors
| Vibration | X | X | Visually check refrigeration compressors and compressor rack for visible siqns of vibration
| Oil Residue | X | X | Visually check refrigeration compressors, refrigeration compressor rack, and condensinq units for visible siqns of oil residue
| Excessive Heat |  | X
| Oil Level | X | X | Look at each sight glass and verify that oil level is between 1/3 and 1/2 of glass
| Foam in Oil | X | X | Look at each sight glass for foam.
| Looseor missing Covers | X | X | Look at all cover, cover plates, etc.
| Noise Level | X | X
| Valve Caps | X | X | Look at each valve and ensure that all valves have valve cap in place
| Test refrigeration system for non-condensibles |  | X
| Execute oil acid test |  | X
| High/Low Pressure Switches | X | X | Verify settings and operation of switch
| Oil Failure Switch | X | X | Verify settings and operation of switch
| Check oil pressure |  | X | Confirm within manufacturer's recommendations
Air Cooled Condenser
| Fan motor | X | X | Look at condenser fan to verify that it is rotating
| Fan guards | X | X | Inspect for broken, missing, or loose fan guards
| Loose panels/components | X | X | Inspect all panels and covers
| Valve caps | X | X | Inspect all valves to ensure that valve caps are in place
| Clean or dirty? | X |  | Inspect inlet side of condenser for dirt, cotton, or other debris that will impact air flow
| Fin condition | X |  | Inspect condenser coil surface for damaged or loose fins
| Air flow? | X | X | Verify that air can flow/ is flowing through condenser
| Clean Condensers |  | X | Contractor to pressure wash condenser
| Pressure switches | X | X
| Fan Cycling/ condenser split | X | X | If system is so equipped, verify operation and settings
| Sensors/Transducers intact |  | X | If system is so equipped, verify that temperature sensors are attached to piping
Oil Reservoir/ Oil Separator
| Inspect oil reservoir/oil separator | X | X | Inspect vessle for oil residue
| Verify oil level | X | X | Look at sight glass and verify oil level
Filter Driers
| Change Driers |  | X
Suction Filters
| Change Filters |  | X
Oil Filters
| Change Oil Filters |  | X
Cooler/Freezer Boxes
| Condensation issues | X | X | Inspect interior, and exterior of box for condensation issues or ice build UD
| Ice build up an floor | X | X | Inspect freezer floor along walls, and across doorways for ice build up
| Door gaskets | X | X | Inspect door gasket for signs of damage, tears, or flattening
| Door sweeps | X | X | Verify that door sweeps on cooler or freezer doors drag on the floor
| Door closure mechanism | X | X | Verify operation of door closure mechanism
| Latch and strike (inside and outside) | X | X | Inspect door latch and strike to ensure operation and that when closed, door is held tiaht to door fram
Strip Curtains
| Inspect for Damage | X | X | Inspect door curtains for signs of damage
Evaporators
| Inspect of ice buildup | X | X | Inspect each evaporator for signs of ice build up
| Fans spinning | X | X | Inspect each evaporator fan to ensure operation
| Fan guards | X | X | Inspect for broken, damaged, or loose fan guards
| Vibration | X | X | Inspect fan motor and fan assembly for vibration
| Fan bearing noise | X | X | Listen to each fan motor for bearing noise
| Fan rotation direction | X | X | Verify fan rotation
| Coil damage/ fin condition | X | X | Inspect each coil sheet for damage
| Is the evaporator dirty |  | X | Check to see if evaporator coil is dirty
| Cleaning of evaporators |  | X
Evaporator Drain Lines
| Drains clean |  | X
| Heat tape operation | X | X | Verify operation of heat tape
Piping System
| Vibration |  | X | Visually inspect refrigeration piping system and look specificall for vibration, shakinq, movement, torn insulation
| Torn insulation |  | X | Visually inspect piping system for signs of torn insulation
| Condensation/Ice build up |  | X | Inspect piping system for signs of moisture, ice build up
| Hangers- verify pipe is touching hangers, insulation is not crushed, hangers have |  | X | Inspect piping system to ensure that hangers are not damaged and are supporting pipe

## Ice Machine
Follett Ice Maker Model HCC700A PM Maintenance of System and all Affilitated Equipment
|  | Quarterly | Annually | Requirement | Comments
Follett Ice Machine
| Clean and sanitize |  | X
| Replace water filters |  | X

## Sheet1
Montgomery County Schools Storage Facility Zero Zone Racks Blast chiller 4 compressors 4 - RPE48 Suction filters 2 - 4864 liquid filters 1- 303 Oli filter 5 Gallons POE 32 Low Temp Rack 5 compressors 5 - RPE48 Suction filters 2 - 4864 liquid filters 1- 303 Oil Filter 6 - Gallons POE 32 Medium Temp Racks 7 Compressors 7 - RPE48 Suction Filters 4 - RC10098 Liquid Filters 1- 303 Oil Filter 8-Gallons POE oil 20 Medium temp evap coils 35 Low Temp freezer coils
1- Ice Machine with 3 14000 Everpure water filters